## Part_1_Connected_Load
Load Description | Connected Load (W)
Lighting (2400 × 3W/ft²) | 7200
Small Appliance Circuits (2×1500) | 3000
Laundry Circuit | 1500
Electric Range | 12000
Dryer | 5000
Air Conditioner | 3500
Total Connected Load (W) | 32200

## Part_2_Demand_Factor
Description | Value
Total Connected Load (W) | 32200
First 10kW @100% | 10000
Remaining Load @40% | 8880
Adjusted Demand Load (W) | 18880

## Part_3_Current_Calculation
Description | Value
Adjusted Demand Load (W) | 18880
System Voltage (V) | 240
Calculated Current (A) | 78.6667